# FIRST DRAFT

#### Government Notice

# MINISTRY OF LABOUR, INDUSTRIAL RELATIONS & EMPLOYMENT CREATION

No. …..										2021

LABOUR ACT, 2007

AMENDMENTS OF THE REGULATIONS RELATING TO THE HEALTH AND SAFETY OF EMPLOYEES AT WORK, 1997

The Minister has, after consultation with the Labour Advisory Council, under section 101 of the Labour Act, 2007 (Act No. 11 of 2007) made, with effect from [date], the regulations set out in the Schedule.

SCHEDULE

1. In these regulations “the Regulations” means the Regulations relating to the Health and             Safety of Employees at Work promulgated by Government Notice 156 of 1 August 1997.

2.  Regulation 258 of the Regulations is amended by insertion of the Regulations below

ELECTRICAL INSTALLATION REGULATIONS

- Definitions

In these regulations,

“Accreditation Authority” means the South African National Accreditation System (SANAS) established by section 3 of the Accreditation for Conformity Assessment, Calibration and Good Laboratory Practice Act, 2006 (Act No. 19 of 2006);

"Act" means LABOUR ACT, 2007 (ACT NO. 11 OF 2007) and any word or expression to which a meaning has been assigned in the Act has such meaning and, unless the context otherwise indicates differently;

"certificate of compliance" means:

(a) a certificate with a unique number obtainable from the Chief Inspector, or a person

appointed by the Chief Inspector, in the form of Annexure 1 and issued by a registered person in respect of an electrical installation or part of an electrical installation; or

(b) a certificate of compliance issued under the Electrical Installation Regulations 2021

“Chief Inspector” means an inspector appointed under Section 124 of Labour Act 2007 (Act No. 11 of 2007), and holding the position of Chief Inspector of Occupational Health and Safety in the Ministry of Labour, Industrial Relations and Employment Creation;

“Competent person” means a person certified in writing by the Chief Inspector with sufficient knowledge and skills of applicable standards, capable of identifying workplace hazards related to specific operation, and has the authority to correct them;

"Electrical contractor" means a person registered to perform electrical installation work. Who undertakes to perform electrical installation work on behalf of any other person but excludes an employee of such first mentioned person;

"electrical installation" means the entire electrical installation on a customer’s premises, including all material, equipment and appliances used or intended to be used for or in connection with the provision of electricity from a point of control to a point of consumption by definition includes only up to the supply terminal of appliances (machinery) anywhere on the premises, including any equipment forming part of such an electrical installation irrespective of whether or not it is part of the electrical circuit, but excluding

(a) any electrical equipment or machinery of the supplier related to the supply of

electricity on the premises;

(b) any electrical equipment or machinery which transmits electrical energy in

telecommunication, control circuits, television or radio circuits;

(c) any processing plant of a mine that is subject to its own specific regulations;

(d) an electrical installation on a vehicle, vessel, train or aircraft; and

(d)  control circuits of 50 V or less between different parts of machinery or system

components, forming a unit, that are separately installed and derived from an

independent source or an isolating transformer;

"electrical tester for single phase" means a person who has been registered as an electrical tester for single phase in terms of regulation for the verification and certification of the construction, testing and inspection of electrical installations supplied by a single-phase electricity supply at the point of control, excluding specialised electrical installations;

"general control" means overseeing electrical installation work that is being carried out, includes instruction, guidance and supervision in respect of that work;

“hazardous location” means a location classified depending on the properties of the flammable vapours, liquids or gases, or combustible dusts or fibres which may be present therein and the likelihood that a flammable or combustible concentration or quantity is present;

"installation electrician" means a person who has been registered as an installation electrician in terms of regulation for the verification and certification of the construction, testing and inspection of any electrical installation, excluding specialised electrical installations;

"installation work" means

(a) the installation, extension, modification or repair of an electrical installation;

(b) the connection of machinery at the supply terminals of such machinery; or

(c) the inspection, testing and verification of electrical installations for the purpose of

issuing a certificate of compliance;

"master installation electrician" means a person who has been registered as a master installation electrician in terms of this Regulation, for the verification and certification of the construction, testing and inspection of any electrical installation;

“national database” means database used for the capturing of all the information necessary in terms of this Regulation.

"point of consumption" means any point of outlet or the supply terminals of machinery which is not connected to a point of outlet and which converts electrical energy to another form of energy: Provided that in the case of machinery which has been installed for any specific purpose as a complete unit, the point of consumption shall be the supply terminals which have been provided on the unit of machinery for that purpose;

"point of control" means the point at which an electrical installation on or in any premises can be switched off/on by a user or lessor from the electricity supplied from the point of supply, or the point at which a particular part of an electrical installation on or in any premises can be switched off/on where different users occupy different portions of such premises;

"point of outlet" means any termination of an electrical installation which has been provided for connecting any electrical machinery without the use of tools;

"point of supply" means the point at which electricity is supplied to any premises by a supplier;

“reasonably practicable safe electrical installation” in relation to an electrical installation that existed prior to the publication of the current edition of the health and safety standard incorporated into these regulations in terms of regulation 7 (1) means that such electrical installation complies with the general safety principles of such standard;

"registered person" means a person registered in terms of the Electrical Installation Regulations, 2018, as an electrical tester for single phase, an installation electrician or a master installation electrician, as the case may be;

“SANS” means South African National Standards;

"specialised electrical installations" means electrical installations in

(a) explosive atmospheres as contemplated in SANS10086-1;

(b) the petroleum industry as contemplated in SANS 1 0089-2;

(c) hazardous locations as contemplated in SANS 10108; or

(d) medical locations as contemplated in SANS10142-1, published by Standards

South Africa;

"supplier" in relation to a particular electrical installation, means any person who supplies or contracts or agrees to supply electricity to that electrical installation;

"supply terminals" in relation to machinery installed as a complete unit, means the terminals or connection clamps on such machinery where the external conductors supplying the machinery with electricity are terminated or connected;

“technical working group” means a technical working group established in terms   of regulation 3;

“User” means a person responsible for the safety, safe operation and maintenance of the electrical installation he or she uses or leases;

- Scope of application

- These regulations shall be applicable to users or lessors, approved inspection authorities for electrical installations, registered persons, electrical contractors, suppliers, designers and to suppliers of materials and other electrical articles or parts thereof whether temporary, permanent, or in a stationary or mobile state and installation.

- Establishment of technical working group for Electrical Installation Regulations

- The chief inspector may establish one or more technical working groups to advise the him or her on any matter relating to these Regulations.

(2) A member of a technical working group shall be appointed by the chief inspector             by reason of his or her knowledge of the matter for which the technical working group is established.

(3) A member of a technical working group who is not an officer may be remunerated from money appropriate for such purpose by the Minister.

(4) The chief inspector shall appoint the technical working group members for such period as he or she may determine at the time of appointment: Provided that the chief inspector may discharge a member at any time, for reasons that are fair and just, and appoint a new member in his her or her place.

(5) The chief inspector may co-opt any person or persons who have specialized      knowledge of any matter dealt with by a technical working group.

(6) A technical working group shall conduct its work in accordance with the instructions and rules of conduct set by the chief inspector.

4. Responsibility for electrical installations

(1) Subject to sub regulation 4 (3), the user of an electrical installation, as the case may be, shall be responsible for the safety, safe use and maintenance of the electrical installation he or she uses or leases, except for work as permitted in regulation 11 (3), shall not tamper with or allow any tampering on any installation whether or not a certificate of compliance has been issued.

(2) The user of an electrical installation, as the case may be, shall be responsible for the safety of the conductors on his or her premises connecting the electrical installation to the point of supply in the case where the point of supply is not the point of control.

(3) Where there is a written undertaking between the owner and a lessee/user whereby the responsibility to ensure compliance and the safety of the electrical installation has been transferred to the lessee/user, the lessee/user shall be responsible for that installation as if he or she were the owner.

5. Approved inspection authorities for electrical installations

(1) The Chief Inspector shall approve any person that has been accredited by the

Accreditation Authority as an Approved Inspection Authority for electrical installations.

(2) An application to be an approved inspection authority shall be made to the Chief Inspector in the form of Annexure 2 together with;

(a) such documentations as the Chief Inspector may requires; and

(b) the fee prescribed by regulation 16.

(3) An approved inspection authority for electrical installations shall inform the Chief Inspector of any change affecting its approval in terms of these Regulations within 14 days after such change.

6. Functions of approved inspection authorities for electrical installations

(1) An approved inspection authority for electrical installations may enter premises and conduct an inspection, test or investigation only when;

(a) contracted by the Chief Inspector or any person acting on his or her behalf for a

specific electrical installation; or

(b)  contracted by the Chief Inspector for any other specific function

(c)   requested by the user of an electrical installation to do so.

(2)  An approved inspection authority for electrical installations may not operate as an electrical contractor.

(3)  An approved inspection authority shall only inspect the type of electrical installation for which they have been accredited by the Chief Inspector.

(4)  An approved inspection authority for electrical installation shall be accountable and abide by the codes of conduct determined by the Chief Inspector

(5)  An approved inspection authority shall submit reports to the persons referred to in 1 (a) (b) and (c) respectively.

(6) Where an inspection, test or investigation has been conducted by an Approved Inspection Authority and where faults or defects in the opinion of the approved inspection authority for electrical installation constitutes an immediate danger to persons and animals or damage to property, that approved inspection authority may notify the registered person or electrical contractor responsible for such faults and defects to rectify such faults and defects in a period specified by the Chief Inspector.

7. Design and construction

(1) Incorporated standards referred to in this regulation shall be the relevant standards issued by the Namibian Standards Institute.

(2) No person may authorise, design, install or permit or require the installation of an

electrical installation, other than in accordance with a health and safety standards

incorporated into these regulations.

(3) No person may use components within an electrical installation unless those components comply with the standards referred to in the relevant incorporated standard referred to in sub regulation 7(1), and proof of compliance shall be identifiable on the components or certification shall be available from the manufacturer or supplier of the materials or components.

(4) Items of an electrical installation not covered by an incorporated health and safety

standard, and the conductors between the point of supply and the point of control, shall be installed in accordance with the by-laws or regulations of the supplier concerned.

(5) A registered person shall exercise general control over all electrical installation work being carried out, and no person may allow such work without such control.

(6) Where the voltage exceeds 1 kV, a person deemed competent in terms of paragraphs of the definition of a competent person or a person registered in a professional category in terms of the Engineering Council of Namibia shall approve the design of that part of an electrical installation.

(7) Where the intention is to supply 25KVA or five or more electrical installations on the same premises from a new point of supply or separate new points of supply, the user shall appoint either an Approved Inspection Authority or a competent person who also complies with the provisions of Regulation 12(2) or a person registered in a professional category (in terms of the Engineering Council of Namibia), and who complies with the provisions of Regulation 12(2) who shall ensure the compliance contemplated in sub regulation 10 (1) from the commencement to the commissioning of the electrical installation.

(8) No supplier may restrict the application of a health and safety standard referred to in sub regulation 11 (2) (b) when an electrical installation is installed, except where the distribution system of the supplier may be adversely affected by the application thereof.

8. Electrical contractor

(1) No person may do electrical installation work as an electrical contractor unless that person has been registered as an electrical contractor in terms of this Regulation.

(2) Any person who does electrical installation work as an electrical contractor shall register annually in the form annexure 7 with the Chief Inspector or a person appointed by the Chief Inspector.

(3) An application for registration as referred to in sub regulation 8 (1) shall be accompanied by the fee prescribed by regulation 16.

(4) The Chief Inspector or a person appointed by the Chief Inspector shall register any

person referred to in sub regulation as an electrical contractor and enter such registration into the national database, provided that such person

(a)	has a fixed address; and

(b)	employs a registered person in a full-time capacity or is himself or herself a registered person

9. Certificate of compliance

(1) Subject to the provisions of this sub regulation (3), every user of an electrical installation, as the case may be, shall have a valid certificate of compliance for that installation in the form of Annexure 1, which shall be accompanied by a test report in the format approved by the Chief Inspector, in respect of every such electrical installation.

(2) Subject to the provisions of sub regulation (3), every user of an electrical installation, as the case may be, shall on request produce the certificate of compliance for that electrical installation to an inspector, a supplier or, subject to regulation 6(1) an approved inspection authority for electrical installations.

(3) Sub regulation (1) shall not apply to an electrical installation that existed prior to 1 July 2021, and where there was no change of ownership after 1 July 2021: Provided that, if any addition or alteration is effected to such an electrical installation, the user of the electrical installation, as the case may be, shall obtain a certificate of compliance for the whole electrical installation, where after the provisions of sub regulation 7 (3) shall be applicable to such electrical installation.

(4) Where any addition or alteration or repair has been effected to an electrical installation for which a certificate of compliance was previously issued, the user of such electrical installation shall obtain a certificate of compliance for at least the addition or alteration or repair.

(5) Subject to the provisions of this regulation, the user may not allow a change of ownership if a new valid certificate of compliance is not issued.

(6) The relevant supplier may at any reasonable time inspect or test any electrical installation:

Provided that the supplier shall not charge any fee for such an inspection or test unless the inspection or test is carried out at the request of the user or lessor.

(7) If an inspector, an approved inspection authority for electrical installations or supplier has carried out an inspection or test and has detected any fault or defect in any electrical installation, that inspector, approved inspection authority for electrical installations or supplier may require the user of that electrical installation to obtain a new certificate of compliance:

Provided that if such fault or defect in the opinion of the inspector, approved inspection

authority for electrical installations or supplier constitutes an immediate danger to persons and animals or damage to property, that inspector, approved inspection authority for electrical installations or supplier shall forthwith take steps to have the supply to the circuit in which the fault or defect was detected, disconnected: Provided further that where such fault or defect is of such a nature that it may indicate negligence on the part of a registered person, the inspector, approved inspection authority for electrical installations or supplier shall forthwith report those circumstances in writing to the Chief Inspector.

10. Commencement to do installation work and permission to connect to electrical supply

(1) No person shall commence installation work which requires a new supply or an increase in electricity supply capacity unless the supplier has been notified thereof in terms of annexure 4. Failure to notify the supplier will result in a penalty fee of N$150.00 per day.

(2) No person shall connect or permit the connection of any completed or partially completed

electrical installation to the electricity supply unless it has been inspected and tested by a

registered person and a certificate of compliance for that electrical installation has been

issued: Provided that the supplier may on request connect the supply to the electrical

installation for the purpose of testing and the completion of the certificate of compliance by a registered person: Provided further that this sub regulation 10 (2) shall not apply in a case where the electricity was disconnected for the non-payment of the electricity account or where there has been a change of tenant but not of ownership.

11. Issuing of certificate of compliance

(1) No person other than a registered person may issue a certificate of compliance.

(2) A registered person shall issue a certificate of compliance accompanied by the required test report only after having satisfied himself or herself by means of an inspection and test that;

(a) a new electrical installation complies with the provisions of regulation and was carried out under his or her general control; or

(b) an electrical installation which existed prior to the publication of the current edition of

the health and safety standard incorporated into these Regulations in terms of

regulation, shall comply with the general safety principles of such standard; or

(c) an electrical installation referred to in paragraph 2 (b), to which extensions or

alterations have been effected, provided that

(i)   the existing part of the electrical installation complies with the general safety

principles of such standard and is safe, and

(ii) the extensions or alterations effected comply with the provisions of regulation

7(2) and were carried out under his or her general control.

(3) If at any time prior to the issuing of a certificate of compliance any fault or defect is detected in any part of the electrical installation, the registered person shall refuse to issue such certificate until that fault or defect has been rectified: Provided that if such fault or defect in the opinion of the registered person constitutes an immediate danger to persons in a case where electricity is already supplied, he or she shall forthwith take steps to disconnect the supply to the circuit in which the fault or defect was detected and notify the Chief Inspector thereof.

(4) Any person who undertakes to do electrical installation work shall ensure that a valid

certificate of compliance is issued on completion of such work

(5) No person may amend a certificate of compliance.

12. Application for registration as a registered person

(1) An application for registration as a registered person shall be made to the Chief Inspector in the form of Annexure 3, together with the registration fee prescribed by Chief Inspector from time to time. All documents required as per the registration criteria shall be first verified by Namibia Qualifications Authority (NQA).

(2) Any natural person who satisfies the Chief Inspector that he or she meets the registration criteria and:

(a) has relevant knowledge of the rules applicable to electrical installations in the category for which the application is being made; and

(b) has appropriate practical experience in respect of the electrical installation, verification and certification of the construction, testing and inspection of the type of electrical installation for which application is being made; Shall be registered as an electrical tester for single phase, an installation electrician, or a master installation electrician, as the case may be.

(3) The Chief Inspector shall furnish a registered person with the appropriate certificate of registration and enter such registration into the national database.

(4) A registered person shall on request produce his or her certificate of registration to an inspector, an approved inspection authority for electrical installations, a supplier or any person to whom he or she intends to issue a certificate of compliance.

(5) A registered person shall inform the Chief Inspector of any changes affecting his or her registration within 14 days after becoming aware of such change.

13. Substitution of lost, damaged or destroyed certificate

(1) If any registration certificate issued in terms of these regulations to an electrical contractor or a registered person is lost, damaged or destroyed, the person to whom the certificate was issued may apply to the Chief Inspector for a duplicate certificate in the form of Annexure 6, together with the relevant registration fee prescribed by regulation.

(2) After proof that a certificate referred to in sub regulation 13 (1) has been lost, damaged or destroyed has been submitted to the satisfaction of the Chief Inspector, the Chief Inspector shall issue a duplicate thereof on which the word "duplicate" shall appear.

14. Withdrawal of registration and approval

(1)  Subject to the provision of sub regulation (2) the Chief Inspector may withdraw or suspend an approval issued to an approved inspection authority, a registration issued to an electrical contractor or a certificate of registration issued to a registered person if such a person

(a)  no longer complies with any of the conditions referred to in regulations 3(2)(a), 6(4) or 11(2) respectively; or

(b)  is convicted of an offence referred to in regulation 17

(2)   The Chief Inspector may not withdraw a registration or an approval unless he or she has;

(a) informed the holder of such regulation or approval of the intended withdrawal thereof and the grounds upon which it is based; and

(b) afforded such a holder reasonable opportunity to state his or her case and if the holder is a person contemplated in sub regulation 5(1), afforded such holder an opportunity to comply with those conditions within the period specified by the Chief Inspector.

(3) The Chief Inspector shall, in writing, inform the person concerned of reasons for his or her decision.

(4)  Any person adversely affected by a decision of the Chief Inspector may in writing, appeal to the Permanent Secretary in the Ministry of Labour, Industrial Relations and Employment Creation against such decision.

(5)  An appeal referred to in sub regulation (4) above, shall;

(a)  be lodged within thirty days from the date on which the decision was made known; and

(b) set out the grounds of appeal.

(6) After considering the grounds of appeal and the Chief Inspector’s reasons for his or her decision, the Permanent Secretary in the Ministry of Labour, Industrial Relations and Employment Creation shall as soon as practicable confirm, set aside or amend the decision.

15. Disputes

(1) Should a dispute arise over the interpretation of any provision of these regulations between a user, a registered person, an electrical contractor, an approved inspection authority for electrical installations or a supplier, as the case may be, an affected person may approach the Chief Inspector for an interpretation of the matter.

(2) A person who refers a dispute referred to in this Regulation shall serve a written notice of dispute, setting out fully the nature and grounds of the dispute, on both the Chief Inspector and the person whose interpretation he or she is disputing, by personally delivering the notice of dispute or sending it by registered post.

(3) The person whose interpretation is disputed shall within 14 working days of the date on which he or she received the notice of dispute, forward a notice in writing setting out the reasons for his or her interpretation to the Chief Inspector.

(4) The Chief Inspector shall as soon as practicable, after having considered the grounds and the cause of the dispute, confirm, set aside or vary the interpretation of the safety standard in question or substitute it for the interpretation, which in the opinion of the Chief Inspector, ought to have been given.

16. Fees payable

The applicable application, registration and licence renewal fees shall be as determined by the Chief Inspector in consultation with the Labour Advisory Council.

17. Offences and penalties

Any person who contravenes or fails to comply with any of the provisions of regulations shall be guilty of an offence and liable upon conviction to a fine or to imprisonment as determined by the Chief Inspector.

Annexure 1

Ministry of Labour, Industrial Relations and Employment Creation

LABOUR ACT, 2007 (ACT NO. 11 OF 2007)

| Certificate of compliance in accordance with Regulation 7 (1) of the Electrical Installation Regulations 2021 | Certificate number |  |
| --- | --- | --- |
|  | Certificate Type (Tick the appropriate block) Initial Certificate Supplementary Certificate Initial Certificate number: …………………………………………………….. Supplementary Certificate: ………………………………………………….…. Issued on:………………………………………………………………………… |
| Identification of the relevant electrical installation (Address or other unique reference, where applicable) Physical address Suburban Town/City Name of building Erf/Lot No GPS Co-ordinates |
| Declaration by registered person I, ....................................................................................... ID No. ....................................................... , a registered person, declare that I have personally carried out the inspection and testing of the electrical installation described in the attached test report as per the requirements of: (Tick the appropriate box) |
| Electrical Installation Regulation 9(2) (a) – (new electrical installation); or |
| Electrical Installation Regulation 9(2) (b) – (existing electrical installation); or |
| Electrical Installation Regulation 9(2) (c) – (new part to existing electrical installation) |
| and deem the electrical installation to be reasonably safe when properly used. I have entered the number of this certificate on the attached test report(s). I declare that the persons responsible for the design, specification, procurement, construction, commissioning and inspection and test have completed the relevant sections of the test report. |
| Registered person registration number: …………… Date of registration: ………………………………….. Type of registration (Tick the appropriate box) Electrical Tester for single phase Installation Electrician Master Installation Electrician Signature:……………….. Date: ………………… | Contact details of Registered person: Telephone No: ……………………………………….. Fax No: ……………………………………………..… Mobile No: ………………………………….……..….. Email: ……………………………..…….………….…. Address: …………………..…………………….……. ………………………………………………………… …………………………………………………………. …………………………………………………………… |
| Note: | This certificate is not valid unless all the sections have been completed correctly and the test report in the format approved by the Chief Inspector is attached. This certificate will be invalid if any corrections have been made. |
| Recipient name:………………………………………..… Signature:…………………….. Date: …………………… |

Annexure 2

APPLICATION FOR APPROVAL AS APPROVED INSPECTION AUTHORITY FOR ELECTRICAL INSTALLATIONS

Ministry of Labour, Industrial Relations and Employment Creation

Division of Occupational Health and Safety

P Bag 19005

Khomasdal

Windhoek

Dear Sir/Madam,

I the undersigned hereby apply to be registered as an approved inspection authority for electrical installations in terms of Electrical Installation Regulations 2021. I declare that the particulars given hereunder are, to the best of my knowledge and belief, correct.

- Particulars of the applicant:

Surname: …………………………………………

First name: ………………………………………

ID number: ………………………………………

Postal address.…………………………………………………

Physical address: ………………………………………………

Name of company: ………………..……………………………

Registration number: …………………………..

Trading as: …………..………………………………

Business postal address.………………………….…………………..…………………...

Business physical address: ……………………….……………………….………………

Telephone No. …..………………………………   Fax No. …………………..……..……….….

Cell ……….……………………………     Email ………………………………………………….

- Scope of approval (Tick appropriate block (s)):

|  | Electrical tester for single phase |  |
| --- | --- | --- |
|  | Installation Electrician |  |
|  | Master Installation Electrician |  |

- Supporting documents

- Certified copy of ID of registered person(s),

- Certified copy of business registration certificate,

- Certified copy of registration certificates of registered person(s),

- Certified copy of accreditation certificate from accreditation authority.

Signature of the applicant:…………………………………………….  Date: …………………….

FOR OFFICIAL USE ONLY

Application: APPROVED/NOT APPROVED

Reason/s for refusal: ………………………………………………………………………………………………………………………………………………………………………………………………………………………………

Signature:………………………………………   Designation:…………………………...………

Registration number: …………………………   Renewal date:………………….……..……….

Date of issue: …………………………………

Annexure 3

APPLICATION FOR REGISTRATION AS A REGISTERED PERSON

Ministry of Labour, Industrial Relations and Employment Creation

Division of Occupational Health and Safety

P Bag 19005

Khomasdal

Windhoek

Dear Sir/Madam,

I the undersigned, hereby, in terms of regulation 10(1) of the Electrical Installation Regulations 2021, apply to be registered as electrical tester for single phase*/installation electrician*/master installation electrician* and hereby declare that the particulars given hereunder are correct, to the best of my knowledge and belief, correct. I further declare that I know of no reason why I should not be regarded as being physically able to inspect and test electrical installations.

(* Delete whichever is not applicable).

I attach two photographs of myself as required by the Chief Inspector.

Yours faithfully,

……………………………………                               …………………………….

Signature 						Date

Notes:

- The applicant must also sign this form in the three spaces provided for specimen signatures at the end of this form.

- The chief inspector requires the submission of two clear identical photographs of 40 mm by 30 mm showing the face and shoulders of the applicant. (The photographs required are similar to those required for a passport and can be obtained from any photographer who renders such a service.)

- The application fee is N$200,00

Surname (block letters)…………………………………………………….………………

First names (block letters)……………………………………………….…………………

Postal address.………………………………………………………..……..………………

Telephone No. (W)..……………………………………….

(Fax)………………………….………………		(Cell)………………………………….………

(Email) …………….…………………………

Date of birth ……………………………………………...

Place of birth…………………………………..…………..

Identity no.: …………………………………..…………..

Details of training appropriate to installation work:

Note: Applicant must hereunder submit with the application, testimonials form employees stating the duration and nature of the training.

- Training other than under a contract of apprenticeship in terms of the Vocational Training Act or …….., in a trade appropriate to electrical installation work

| Name and address of employer |  |
| --- | --- |
| Duration of training | ……. Years | From: / / | To: / / |

- Apprenticeship or training in terms of the ………. Act, in a trade appropriate to electrical installation work

No. of contract …………………….   Trade in which trained ………..………………………….

| Name and address of employer |  |
| --- | --- |
| Duration of training | ……. Years | From: / / | To: / / |

On job attachment, details of practical experience other than referred to above.

| Name and address of employer |  |
| --- | --- |
| Duration of training | ……. Years | From: / / | To: / / |

*Certified copies of certificates and diplomas to be attached

# SPECIMEN SIGNATURE OF APPLICANT

Note ( The specimen signatures should be the normal signature of the applicant and should be carefully completed. One specimen will be affixed to any certificate of registration that may be issued.

1	2	3

##### FOR OFFICE USE ONLY

Application: APPROVED/NOT APPROVED

Reason/s for refusal: ………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………

Registration No.:……………………………………              Date: ………………………………….…………..

Signature:…………………………….……………		Designation:…………….……..……………….…

Annexure 4

REGULATION 8 (1) OF THE ELECTRICAL INSTALLATION REGULATIONS, 2021

NOTICE FOR COMMENCEMENT OF INSTALLATION WORK

Name of the supply authority: ………………………………………………………………………………………………………

Address of the supply authority: ……………………………………………………………………………………………………….……………………………..……………………………….…………………….

I hereby advise that electrical installation work will commence at:

Erf no: ……………………………………………………………. 	Township: ……………………………….

Street address: ………………………………………………………………………………………………………

Name of the building: ………………………………………………   Floor: ………………………………..……

Name of the tenant/occupier/agent/owner:

…………………………………………………………………………………………………………………………

Note: Farms & agricultural holdings, full description as per title deed required.

………………………………………………………………………………………………………………….………

Description of proposed work:

………………………………………………………………………………………………………………………….

Date of commencement of installation work:

………………………………………………………………………………………….………………………………

Anticipated date of completion:

………………………………………………………………………………………………..………………………..

Tick in the applicable box

| New installation |  | Extension |  | Modification |  |
| --- | --- | --- | --- | --- | --- |

Size of the installation………………..kVA/ Amps      Three phase:            Single phase:

Electrical Contractor/Registered person*:………………………………………………………….…………….

(block letters)

Name of representative: ……………………………………………………………………………..…..…….…..

Fixed address:…………………………………………………………………………………………....…………..

Registered person’s Registration Certificate No*.:…………………………………………….………………….

Signature:……………………………..……………    	Office telephone no.:………………………………

Fax no.:…………………….………………………...          Cell no.:………………………………………………

Email: ………………………………….……………………………………………………………………………...

Annexure 5

APPLICATION FOR DUPLICATE CERTIFICATE ISSUED IN TERMS OF THE ELECTRICAL INSTALLATIONS 2021

Ministry of Labour, Industrial Relations and Employment Creation

Division of Occupational Health and Safety

P Bag 19005

Khomasdal

Windhoek

Dear Sir/Madam,

I the undersigned hereby apply for a duplicate certificate of registration issued to me in terms of regulations 5 (2), of the Electrical Installation Regulations, 2021. I declare that the particulars given hereunder are, to the best of my knowledge and belief, correct.

- Particulars of applicant: (block letters)

Surname: …………………………………… First name: ……………………………………………..

ID number: ………………………………….  Previous Registration No. ……………………………

Postal address.…………………..………..……………..…………………………………...…..………

Physical address: …………………………………..………………………………………….…………

Telephone No. ...………………..…………………       Cell No. ………………………………...…….

Fax. ……………………………………..  E-mail. ………………………………....…………………….

- Scope of approval:

|  | Electrical tester for single phase |  |
| --- | --- | --- |
|  | Installation Electrician |  |
|  | Master installation electrician |  |

- Supporting documents:

- Certified copy of ID

- Two clear identical photographs of 40 mm x 30 mm showing the face and shoulders of applicant

- No of the lost, damaged or destroyed certificate

Signature of applicant: ……………………………       	Date: ………………………..……….

- Affidavit

FOR OFFICIAL USE ONLY

Re-application: APPROVED/NOT APPROVED

Reason/s for refusal: ……………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………

Signature: ……………………………………..    Designation: …………….………..……………………

Registration number: …………………………    Date: …………………………………

Annexure 6

APPLICATION FOR LICENCE TO OPERATE AS AN ELECTRICAL CONTRACTOR

Ministry of Labour, Industrial Relations and Employment Creation

Division of Occupational Health and Safety

P Bag 19005

Khomasdal

Windhoek

- Particulars of applicant:

Surname ……………………………………..……… 	First name: …………………………

(Block letters)					            (Block letters)

ID number:……………………………………………

Postal address.………………....……………………..…………………………..…..….………..……

Physical address: ………………………………………………………………..……..….……………

Telephone No. (W)..…………………………. 		(H)……………………………..……….…….

(Fax)…………………………………………..		(Cell)………………………………………….

(Email) ………………………………………………………………..…………………………………..

Name of company: ……………………………………………………………………………………….

Registration number: ………………….…………..   	Trading as: ………….……….………………

Business postal address.………………………………………………..……………………..………...

Business physical address: ………………………………………………...……………………………

Telephone No. (W)..………………….……		(H)…………………..………….………..…..…

(Fax)………………………………………..                        (Cell)…………………….….……………………

(Email) ………………………………………………………….……………….…………………………

- State type of registration you have:

- Electrical testers for single phase

- Installation Electrician

- Master Installation Electrician

3.     Where registered person(s) is/are employed on a full-time basis, complete the following: (Section 3 can be filled in as many times as the number of registered person/s employed by the business). Notify the chief inspector in case of any changes.

Surname of Registered Person: ………………………………………….……………..……….……

Name/s Registered Person: ……………………………………………………………………….…..

ID number of Registered Person: ………………………………………………………..……………

Type of registration: TSP/IE/MIE (delete which is not applicable)

Registration Number: ……………………….   	Date issued: …………………………………

4.    In support of your application, please submit the following:

(a) 	Certified copy of your ID and, where applicable, certified copies of ID’s of registered person(s);

(b)	Certified copy of business registration no;

(c)	Certified copy of the relevant registration certificate(s) (both sides).

Signature of the applicant: …………………………………..………………  Date: …………………

FOR OFFICIAL USE ONLY

Application: APPROVED/NOT APPROVED

Reason/sforrefusal: ………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………

Signature: ……………………………………………………………..………………….…..…………..

Designation:……………………………………………………………………………….………………

License number: ……………………………...   Renewal date:……………………………………….

Date of issue: ……………………..……………………………

Annexure 7

| Test Report in conjunction with CoC No. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

|  | Applicable to all installations (Single and three phase) |  | Applicable to Three Phase installations only |
| --- | --- | --- | --- |

| Physical address |  |
| --- | --- |

| INSTALLATION TYPE |
| --- |
| Domestic |  |  | Commercial |  |  | Industrial |  |  | Other |  |
| Sectional title |  |  |  |  |  |  |  |

| CHARACTERISTICS OF SUPPLY TO PART/INSTALLATION COVERED BY THIS REPORT |
| --- |
| Voltage |
| 230V |  |  | 400V |  |  | 525V |  |  | Other |  |  | V |  | AC 50Hz |  |  | DC |  |
| Number of phases |
| Single phase |  |  | Split phase |  |  | Three phase (3 wire) |  |  | Three phase (4 wire) |  |
| Earthing |
| Earth terminal provided by supplier | Yes |  |  | No |  | Earthing system (if source is accessible) | TN-S |  |  | TN-C-S |  |
| Alternative supplies connected to the installation/part installation covered by this report |
| Generating set |  |  | Batteries (UPS) |  |  | Other |  |  | Output | Phase | KVA |
| Alternative supply is connected to | Complete installation |  |  | Part installation |  |
| Transfer switching | Number of poles |  |  | Automatic |  |  | Manual |  |  | Plug connector |  |

| DESCRIPTION OF INSTALLATION OR PART INSTALLATION COVERED BY THIS REPORT |
| --- |
| Premises occupied. |  |  | Premises not occupied |  | At the time of certification |
| New installation, excluding specialised installations as listed. (Total installation) |  |
| Existing installation, excluding specialised installations as listed. (Total installation i.e. for Transfer of ownership) |  |
| Part installation. (Where an existing installation is affected by maintenance, i.e. geyser replacement) |  |
| Part installation. (Addition to an existing installation) |  |
| Part installation. (Modification or alteration to an existing installation) |  |
| Temporary installation. |  |
| Construction/installation work in progress likely to affect or change the installation. (If applicable) |  |
| Further/future electrical installation work required. I.e. Connection of plant, machinery or equipment. (if applicable) |  |
| Specify |
| Is any part of the installation at a voltage above 1kV? Yes No If yes, competent person to approve design and complete additional test reports Is this installation one of five or more on the same new supply Yes No If yes, name of the competent person who supervised the installation Notes on installation/part installation covered by this report; |
| Specialised installations not covered by this report (List); |
| Notes on parts of the installation not covered by this report; |

| NUMBER OF POINTS AND CIRCUITS COVERED BY THIS TEST REPORT | Part 1___ of _____ |
| --- | --- |
| Dist. board identification |  |  | Location |  |

Main switch type

| Switch-disconnector |  |  | Circuit breaker |  |  | Earth leakage switch-disconnector |  |  | Earth leakage circuit breaker |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fused switch |  |  | Number of poles |  |  | Current rating | A |  | Short circuit withstand rating | KA |

Circuits

| Lighting |  |  | Cooking appliance |  |  | Motor Control Centre |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Socket outlets (Single phase) |  |  | Swimming pool/Jacuzzi |  |  | Socket outlets (Three phase) |  |
| Socket outlets (Critical applications) |  |  | Pump |  |  | Step up transformer |  |
| Air conditioner |  |  | Electric fence |  |  |  |  |
| Heater |  |  | Other appliances |  |  |  |  |
| Gate/door motor |  |  | Fixed machinery |  |  |  |  |
| Water heater (geyser) |  |  | Sub Dist. Board |  |  |  |  |

Points supplied from the above circuits

| Lighting |  |  | Water heater (geyser) |  |  | Fixed machinery isolating points |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Socket outlets (Single phase) |  |  | Cooking appliance |  |  | Socket outlets (Three phase) |  |
| Socket outlets (Critical applications) |  |  | Fixed or stationary appliances |  |  |  |  |
| Air conditioner |  |  | Electric fence |  |  |  |  |
| Heater |  |  | Isolating points for appliances |  |  |  |  |
| Door opener |  |  | Sub Dist. Board |  |  |  |  |
| Gate motor |  |  | Fixed machinery |  |  |  |  |
| Step down transformer |  | Earthing system | TN-S |  |  | TN-C-S |  |

| IT |  |
| --- | --- |

Instrument tests

| Insulation resistance | Ω |  | Resistance of protective (earth bonding conductors) | Ω |
| --- | --- | --- | --- | --- |

| Earth loop impedance at the main switch | Ω |  | Voltage at main switch (No load) | V |
| --- | --- | --- | --- | --- |
| Elevated voltage between neutral and external earth | V |  | Voltage at main switch (On load) | V |
| Pros. Short Circuit Current | KA |  | Measured |  |  | Calculated |  | Phase rotation | Clock |  |  | Anti-Clock |  |
| Number of Earth Leakage devices installed on this board |  |  | All Earth Leakage devices tested and operating within specification |  |
| RESPONSIBILITY |

NOTE – For existing installations, complete only 4.4. For new / altered / temporary installations, if no signature appears in 4.1 to 4.3, the signatory of 4.4 takes responsibility

| 4.1 FOR THE DESIGN OF THE INSTALLATION. I, being the person responsible for the DESIGN of the installation, particulars of which are described in sub regulation 7 of this form, CERTIFY that the work, and MATERIAL SPECIFICATION for which I have been responsible, is to the best of my knowledge and belief in accordance with the Electrical Installation Regulations of the OHS Act. The extent of liability of the signatory is limited to the installation described in sub regulation 7 of this form. |
| --- |
| Name (block letters) |  |  | Professional reg. No |  |
| Position |  |  | ID Number |  |  | Tel. No |  |
| Physical address |  |
| For and on behalf of |  |
| Signature |  |  | Date |  |

| 4.2 FOR THE CONSTRUCTION OF THE INSTALLATION. I, being the person responsible for the CONSTRUCTION of the electrical installation and MATERIAL used there for, particulars of which are described in sub regulation 7 of this form, CERTIFY that the work and material for which I have been responsible, is to the best of my knowledge and belief in accordance with the Electrical Installation Regulations The extent of liability of the signatory is limited to the installation described in sub regulation 7 of this form. |
| --- |
| Name (block letters) |  |  | Registration No |  |
| Position |  |  | ID Number |  |  | Tel. No |  |
| Physical address |  |
| For and on behalf of (Contractor) |  |
| Signature |  |  | Date |  |

| 4.3 COMPLIANCE OF THE INSTALLATION FROM COMMENCEMENT TO COMMISIONING. (To be completed only where the installation is one of five or more installations connected to the same NEW supply). I, being the person responsible for the COMPLIANCE of the installation, particulars of which are described in sub regulation 7 of this form, CERTIFY that the installation was done in accordance with SANS10142-1 |
| --- |
| Name (block letters) |  |  | ID Number |  |
| Physical address |  |
| An approved inspection authority for electrical installations |  |  | Chief inspector’s registration number |  |
| A competent person as defined |  |  | Certificate number |  |
| A professionally registered person |  |  | Category of registration |  |
| Registration number |  |
| Signature |  |  | Date |  |

| 4.4 FOR THE INSPECTION AND TEST OF THE INSTALLATION. I, being the person responsible for the INSPECTION AND TESTING of the electrical installation, particulars of which are described in sub regulation 7 of this form, CERTIFY that the INSPECTION AND TESTING were done in accordance with SANS 10142-1, The results given are correct and the installation complies with the requirements as set out in OH&S Act 83 of 1993, all applicable regulations and codes with particular attention being paid to the items listed in section 5 of this form where these items are applicable to the installation described in section 3 of this form.. |
| --- |
| Name (block letters) |  |  | Registration No |  |
| Position |  |  | ID Number |  |  | Tel. No |  |
| Physical address; |  |
| For and on behalf of (Contractor) |  |
| Signature |  |  | Date |  |

5. RESPONSIBILITY All commodities in the installation comply with the applicable safety standards and recommended performance standards. SANS 10142-1 4.3 All commodities in the installation are correctly selected for intended purpose and installed in accordance with the requirements of SANS 10142-1 and with the manufacturer’s requirements. SANS 10142-1 5 The installation complies with the safety requirements contemplated in SANS 10142-1 5.1. All equipment and circuits are correctly and permanently marked or labelled. Notices pertaining to the safety of the installation are in place and legible. SANS 10142-1 4.5 Protective equipment is selected and installed to offer protection as contemplated in SANS 10142-1 5.2.5. Emergency control and disconnecting devices are selected and installed in accordance with SANS 10142-1 5.2.7.and SANS 10142-1 5.2.8 Electrical equipment can withstand the environmental conditions of the location in which it is installed. SANS 10142-1 5.5 Circuits are arranged in accordance with SANS 10142-1 6.1. Conductors and cables are correctly selected, rated and installed with consideration of the connected load and permissible voltage drop. SANS 10142-1 6.2 Conductors and cables are installed and positioned in accordance with SANS 10142-1 6.3 and SANS 10142-1 6.4. Wire ways are installed in accordance with SANS 10142-1 6.5. All distribution boards comply with the minimum safety requirements described in SANS 10142-1 6.6. All protective devices are of the correct rating and capable of withstanding the prospective fault level. Over current protection, overload protection and short-circuit protection is provided as per the requirements of SANS 10142-1 6.7. Earth leakage protection is provided as required and operates correctly and within specified ratings. SANS 10142-1 6.7, SANS 10142-1 8.7.12 and SANS 10142-1 8.7.13 Disconnecting devices are correctly located and all switchgear switches the live conductors. SANS 10142-1 6.9 Consumer’s earth terminal provided. SANS 10142-1 6.11 Earth continuity conductors are electrically continuous and complies with SANS 10142-1 Table 8.1 SANS 10142-1 6.12 Bonding is continuous and complies with the requirements of SANS 10142-1 6.13 Connection of conductors including earthing and bonding is mechanically sound. SANS 10142-1 6.3.7 Ring circuits are continuous. In respect to the electrical installation fire barriers have been erected. A readily accessible earthing point/s for other services is/are installed, clearly marked and labelled and the position/s indicated on the distribution board. SANS 10142-1 6.11.5 and SANS 10142-1 6.11.6 Alternative supply connections and switching is correct and proper notices and indicators are installed. SANS 10142-1 7.12 The installation complies with all the requirements for zoned areas such as bathrooms, spas, swimming pools ornamental pools and fountains. SANS 10142-1 7.1, SANS 10142-1 7. 2 and SANS 10142-1 7.3

NOTES

- In terms of Namibian legislation the user or lessor of an electrical installation is responsible for the safety of such installation.

- The certificate covers only that part of the installation described in section 3 of this Test report.

- The certificate covers the circuits for fixed appliances, but does not cover the actual appliance, for example stoves, geysers, air conditioning units, refrigeration plant, machinery or light fittings.

- Medical and hazardous locations (specialised installations) require additional Certificates and test reports. (See SANS 10142-1 8.8.2 and 8.8.3)

OCCUPATIONAL HEALTH AND SAFETY REGULATIONS

(AS AMENDED)

REGISTRATION CRITERIA FOR REGISTERED PERSON

- Electrical Tester for Single Phase

A candidate must have:

Minimum practical qualification

a.	Submit proof of having passed:

Prescribed trade test level 3 in terms of both Namibia Training Authority and Namibia Qualifications Authority in the following disciplines:

- Electrician

- Millwright (Electro-Mechanical)

b.	Submit documentary proof of successful completion of unit standards on inspection, testing and certification of single-phase domestic electrical installations as prescribed by the Namibia Qualifications Authority.

c.	Submit proof of having passed Electrical Installation Work at National Trade Test Level 3

Minimum theoretical qualification

a.	Achieved a National Certificate Level 2 or National N2 Certificate with the following compulsory subjects:

- Electrical Trade Theory

- Mathematics

- Engineering Science

Or

b.	Achieved a Grade 11 (Standard 9) Certificate with the following compulsory subjects:

- Electrical Trade Theory

- Mathematics

- Engineering Science

Note 1: The candidate must pass each subject with a minimum of 40%

Note 2: The minimum theoretical subjects could be a combination of Grade 11 and N2 subjects

Knowledge of Statutory requirements

Submit proof of working knowledge of legislation and relevant health and safety standards applicable to electrical installations by having passed the subject Installation Rules as administered by the Department of Education in South Africa.

- Installation Electrician

A candidate must have:

Practical qualification

a. Submit proof of having passed:

Prescribed trade test level 3 in terms of both Namibia Training Authority and Namibia Qualifications Authority in the following disciplines:

    - Electrician

    - Millwright (Electro-Mechanical)

b. Submit documentary proof of successful completion of unit standards on inspection,

testing and certification of three phase industrial/commercial installations as prescribed by the Namibia Qualifications Authority

c. Submit proof of having passed Electrical Installation work at National Trade Test Level 3

Minimum theoretical qualification

a. Achieved a National Certificate level 3 Electrical General or National N3 Certificate with the following compulsory subjects:

1.  Electrical Trade Theory or Electro-technology

2.  Mathematics

3.  Engineering Science

Or

b. Grade 12 (Standard 10) with the following compulsory subjects:

  - Mathematics

  - Science

  - Technical subject  - electrical or an equivalent subject that my include a N3 subject )

Note 1: The candidate must pass each subject with a minimum of 40%

Note 2: The minimum theoretical subjects could be a combination of grade 12 and N3 subjects

Or

c. Submit a Diploma in Electrical Engineering:

1. T3 Diploma (Heavy Current)

2. S4 Diploma (Power Engineering)

3. Government Certificate of Competency (Factories or Mines)

Knowledge of Statutory requirements

Submit proof of working knowledge of legislation and relevant health and safety standards

applicable to electrical installations by having passed the subject Installation Rules as

administered by the Department of Education in South Africa.

- Master Installation Electrician

Route 1

A candidate must have:

Practical qualification

- Be registered as an Installation Electrician for at least two years

- Submit proof of at least five years practical experiences in hazardous locations

- Submit documentary proof of successful completion of unit standards on inspection, testing and certification of specialised electrical installations in hazardous locations as prescribed by the Namibia Qualifications Authority

- Submit proof of Knowledge Evaluation report from a Technical Expert Committee appointed by the Chief Inspector.

Knowledge of Statutory requirements

Submit proof of knowledge of legislation and relevant health and safety standards applicable to electrical installations by having passed the subject Specialised Electrical Installation Codes as administered by the Department of Education in South Africa.

Route 2

A candidate must have:

Practical qualification

- Be registered as an Installation Electrician for at least two years

- Submit proof of at least two years practical experiences in hazardous locations.

- Submit documentary proof of successful completion of unit standards on inspection, testing and certification of specialised electrical installations in hazardous locations as proscribed by the Namibia Qualifications Authority.

Minimum Theoretical qualification

Submit a National N6 Certificate with one of the following subjects:

1.	Electrotechnics

2.  Fault Finding and Protection Devices

3.  Industrial Electronics

Knowledge of Statutory Requirements

Submit proof of working knowledge of legislation and relevant health and safety standards applicable to electrical installations by having passed the subject Specialised Electrical Installation Codes as administered by the Department of Education.

Foreign qualifications

Candidates are required to have all their qualifications evaluated by the Namibia Qualifications Authority.

Documents to be submitted

The following documents must accompany the prescribe application form:

- Proof of practical proficiency (Trade document)

- Proof of theoretical proficiency (Academic records)

- Proof of legal knowledge proficiency (Examinations)

- Proof of unit standards achievements

- Copy of identification document or passport

- Two ID photos (25mm x 30 mm) colour or black and white

- Receipt of payment of application fee

Note: All copies must be certified

ELECTRICAL MACHINERY REGULATIONS, 2019

SCHEDULE

- Definitions

In these Regulations, "the Act" means the Labour Act, 2007 (Act No. 11 of 2007), and any word or expression to which a meaning has been assigned in the Act shall have such meaning and, unless the context otherwise indicates;

"accreditation authority" means the South African National Accreditation System (SANAS) established by section 3 of the Accreditation for Conformity

Assessment, Calibration and Good Laboratory Practice Act, 2006 (Act No. 19 of 2006);

"circuit" means an arrangement of conductors for the purpose of carrying electrical energy;

"conductor" means an electrical conductor so arranged as to be electrically connected to a source of electrical energy;

"confined space" means an enclosed, restricted or limited space in which, because of its construction, location or contents, or any work activity carried on therein, a hazardous substance may accumulate or an oxygen deficient atmosphere may occur, and includes any chamber, tunnel, pipe, pit, sewer, container, valve, pump, sump or similar construction, equipment, machinery or object in which a dangerous liquid or a dangerous concentration of gas, vapour, dust or fumes may be present;

"dead" means at or about zero potential and isolated from any live system;

"earthed" means connected to the general mass of earth in such a manner as will ensure at all times an immediate safe discharge of electrical energy;

"electric fence" means an electrified barrier consisting of one or more bare conductors erected against the trespass of persons or animals;

"electric fence energiser" means electrical machinery arranged so as to deliver a periodic non-lethal amount of electrical energy to an electric fence connected to it;

"electric fence system" means an electric fence and an electric fence energiser;

"insulated" means covered with insulating material of such thickness and properties that it will prevent the flow of electrical energy between the object so covered and its surroundings or any external object in contact with it;

"live" or "alive" means electrically charged;

"miniature substation" means a substation that a person cannot enter;

"portable electric tool" means any electrically operated implement, with the exception of ordinary household electrical appliances, which is designed for use with;

- a flexible cord at the supply end and which is intended for use by hand and which is to be carried by hand at the place of work; or

- a flexible cable at the supply end and which is intended for use by hand and which is to be moved by hand at the place of work;

"registered person" means a person registered in terms of regulation 14 as an electric fence system installer;

"supplier" means any person who supplies or contracts or agrees to supply electricity.

- SCOPE OF APPLICATION

(1) These Regulations shall apply to the designers, manufacturers, installers, sellers, users, employers and suppliers who design, manufacture, install, sell, generate or use electrical machinery.

(2) These Regulations shall apply to users who generate, transmit or distribute electricity whether overhead or underground to the point of supply.

3. Personal protective equipment

An employer or user shall provide free of charge and maintain in good condition such protective equipment as may be necessary to prevent incidents, for use by persons engaged in working on or in close proximity to live electrical machinery or dead electrical machinery which may become live.

- Work on disconnected electrical machinery

Without derogating from any specific duty imposed on employers or users of machinery by the Act, an employer or user shall, whenever work is to be carried out on any electrical machinery which has been disconnected from all sources of electrical energy, but which is liable to acquire or to retain an electrical charge, as far as is practicable, cause precautions to be taken by earthing or other means to discharge the electrical energy to earth from such electrical machinery or any adjacent electrical machinery if there is danger there from before it is handled and to prevent any electrical machinery from being charged or made live while persons are working thereon.

5. Notice

An employer or user shall cause notices to be displayed within, and at all designated entrances to premises, as the case may be, where generating plant and transforming, switching or linking apparatus are situated, which notices shall;

- prohibit unauthorized persons from entering such premises;

- prohibit unauthorized persons from handling or interfering with electrical machinery;

- contain directions of procedure in case of fire; and contain directions on how to resuscitate persons suffering from the effects of electric shock:

Provided that this regulation shall not apply to miniature substations and distribution boxes, on condition that their access doors can be locked or bolted and that only authorized persons are permitted to open them and work thereon.

- Switchgear and transformer premises

(1) An employer or user shall cause enclosed premises housing switchgear and transformers;

  - to be of an ample size so as to provide clear working space for operating and maintenance staff;

  - to be sufficiently ventilated to maintain the equipment at a safe working temperature;

- to be, as far as is practicable, constructed so as to be proof against rodents, leakage, seepage and flooding;

- to be provided with lighting that will enable all equipment, thoroughfares and working areas to be clearly distinguished and all instruments, labels and notices to be easily read;

- to have doors or gates, which can be readily opened from the inside, opening outwards;

- to be provided with fire extinguishing appliances or systems which are suitable for use on electrical machinery and which are maintained in good working order: Provided that, in the case of unattended premises, suitable fire extinguishing appliances be made available at such premises only when work is in progress thereon or therein; and

  - to be of such construction that persons cannot reach in and touch bare conductors or exposed live parts of the electrical machinery.

- No person other than a person authorized thereto by the employer or user shall enter, or be required or permitted by the employer or user to enter, premises housing switchgear or transformers, unless all live conductors are insulated against inadvertent contact or are screened off: Provided that the person so authorized may be accompanied by any other person acting under his control.

- Electrical control gear

(1)  An employer or user shall provide all electrical machinery with controlling apparatus and protective devices which shall, as far as is reasonably practicable, be capable of automatically isolating the power supply in the event of a fault developing on such machinery.

- No employer or user shall place a switch, circuit breaker or fuse in the neutral conductor of a polyphase alternating current or three-wire direct current distribution system unless such switch, circuit breaker or fuse is so arranged as to isolate all phase conductors and the neutral conductor simultaneously:

Provided that this shall not include an isolating link on the neutral conductor installed      for test purposes or to prevent circulating currents.

- The employer or user shall, whenever reasonably practicable, provide switchgear with an interlocking device so arranged that the door or cover of the switch cannot be opened unless the switch is in the 'off position and cannot be switched on unless the door or cover is locked.

(4)  The employer or user shall mark or label all controlling apparatus permanently so as to identify the system or part of the system or the electrical machinery which it controls, and where such control apparatus is accessible from the front and the back these markings shall be on both the front and the back.

- The employer or user shall post a notice at switchgear or control gear which has been switched off or locked out to enable persons to work on electrical machinery or other machinery operated by electricity and controlled by. Such switchgear or control gear, warning against reclosing such switchgear or control gear.

- No person shall act contrary to a warning in terms of sub regulation (5).

8. Switchboards

(1)  An employer or user shall provide an unobstructed space for operating and maintenance staff at the back and front of all switchboards, and the space at the back shall be kept closed and locked except for the purpose of inspection, alteration or repair: Provided that the requirements of this regulation with respect to the unobstructed space at the back of the switchboard shall not apply in the case of -

(a)	switchboards which have no uninsulated conductors accessible from the back;

- switchboards the switchgear of which is of a totally enclosed construction;

- switchboards, the backs of which are accessible only through an opening in the wall or  partition against which they are placed, such openings being kept closed and locked; and

- switchboards which can be safely and effectively maintained from the front and which have all parts accessible from the front.

  - The employer or user shall ensure that all switchboards are selected, designed, manufactured, installed and maintained in accordance with sound engineering practice.

- Electrical machinery in hazardous locations

(1) Every employer or user shall identify all hazardous locations and classify them in accordance with the relevant health and safety standard incorporated into these Regulations under section 44 of the Act.

(2) No person may use electrical machinery in locations where there is danger of fire or explosion owing to the presence, occurrence or development of explosive or flammable articles, or where explosive articles are manufactured, handled or stored, unless such electrical machinery, with regard to its construction relating to the classification of the hazardous locations in which it is to be used, meets the requirements of the safety standard incorporated for this purpose in these Regulations under section 44 of the Act.

  - Every employer or user referred to in subregulation (1) shall be in possession of a certificate in a form acceptable to the chief inspector, which has been issued by an approved inspection authority and in which it is certified that the electrical machinery referred to in subregulation (2) has been manufactured and tested for the groups of dangerous articles in accordance with the relevant health and safety standard incorporated into these Regulations under section 44 of the Act: Provided that in lieu of such certificate an inspector may approve permanent labelling on such machinery, which label shall contain all the relevant information.

    - When diverse items of electrical machinery such as motors, cables and control apparatus are used together to form a system, the employer or user shall ensure that the selection, arrangement, installation, protection, maintenance and working of the system results in no less a degree of safety than when the individual items of such machinery are used separately.

    - The employer or user shall use electrical machinery to which this regulation applies only under such conditions and in such surroundings as prescribed in the health and safety standard referred to in subregulation (2).

    - No employer or user shall effect repairs or adjustments to or otherwise work on electrical machinery under conditions envisaged by subregulation (2) unless such machinery has been rendered dead and effective measures have been taken to ensure that such machinery remains dead.

  - Wherever there is a possibility of the formation of static electricity under working conditions, the employer or user shall earth all metallic structures, machine parts, pneumatic conveyor ducts and pipelines conveying flammable articles and the like, or take such other measures as may be necessary to prevent the formation of electric sparks.

  - The employer or user shall cause all electrical machinery in a hazardous location to be visually inspected and tested at intervals not exceeding two years, any other interval approved by the chief inspector after a risk assessment has been conducted by a person who is competent to express an opinion on the safety thereof: Provided that installed intrinsically safe equipment may in lieu of a test be verified in terms of the approved design.

- The person carrying out the examination referred to in subregulation (8) shall enter, sign and date the results of each examination in a record book which shall be kept by the employer or user for this purpose.

- Portable electric tools

(1) No person shall use or permit the use of a portable electric tool with an operating voltage that exceeds 50 V to earth unless-

- it is connected to a source of electrical energy incorporating an earth leakage protection device, the construction of which meets the requirements of the relevant health and safety standard incorporated into these Regulations under section 44 of the Act; or

- it is connected to a source of electrical energy through the interposition between each tool and the source of an individually double-wound isolating transformer, the secondary winding of which is not earthed at any point and the construction of which meets the requirements of the relevant health and safety standard incorporated into these Regulations under section 44 of the Act; or

- it is connected to a source of high frequency electrical energy derived from a generator which is used solely for supplying energy to such portable electric tool and which arrangement is approved by the chief inspector; or

- it is clearly marked that it is constructed with double or reinforced insulation.

(2) No person shall sell a portable electric tool constructed with double or reinforced insulation referred to in sub regulation (1) (d) unless;-

(a) it is clearly marked that it is constructed with such insulation; and

(b) its insulation is constructed in accordance with the relevant health and safety standard   incorporated into these Regulations under section 44 of the Act,

(3) No employer or user shall use or permit the use of a portable electric tool which is not fitted with a switch to allow for easy and safe starting and stopping of the tool.

(4) The employer or user shall maintain every portable electric tool, together with its flexible cord and plug, in good working order.

- Portable electric lights

(1)  No employer or user shall use or permit the use of a portable light where the operating voltage exceeds 50 V unless;

| (a) | it is fitted with a substantial handle which is made of non-hygroscopic, |
| --- | --- |
|  | non-conducting material; |
| (b) | all live metal parts or parts which may become live owing to a faulty circuit |
|  | are completely protected against accidental contact; |

(c) 	  the lamp is protected by means of a substantial guard firmly fixed to the insulated    handle; and

(d)	    the cable lead-in is such that the insulation can withstand rough use.

- No employer or user shall use or permit the use of a portable electric light in wet or damp conditions or in confined spaces inside metal vessels or when the person is in contact with large masses of metal, unless, subject to the provisions of sub regulation (1)-

  - the lamp is connected to a source of electrical energy incorporating an earth leakage protection device the construction of which meets the requirements of the relevant safety standard incorporated into these Regulations under section 44 of the Act; or

  - the operating voltage of the lamp does not exceed 50 V, and where this electrical energy is derived from a transformer, such transformer shall have separate windings.

- Electric fences

(1) No person shall design, manufacture, sell, install or use an electric fence or electric fence energiser other than in accordance with the relevant health and safety standard incorporated into these Regulations under section 44 of the Act: Provided that electric fences or electric fence energizers installed in accordance with the Electrical Machinery Regulations, 2021, prior to the coming into force of these Regulations shall be deemed to comply with this regulation.

- The seller, importer and manufacturer of an electric fence energizer shall prove compliance with SANS 60335-2-76 by producing a certificate issued by an accredited test laboratory recognized by the accreditation authority.

  - In the case of an electric fence energiser which receives its energy from a battery charged by means of a charging apparatus which receives its power from an electric supply, the user or lessor shall ensure that the charging apparatus is of double-wound isolation construction.

  - Subject to the provisions of subregulation (5), every user or lessor of an electric fence system shall have an electric fence system certificate in the form of Annexure 1 in respect of such electric fence system: Provided that such certificate shall be transferable.

- Subregulation (4) shall not apply to an electric fence system that existed prior to the coming into force of these Regulations: Provided that if-

- any addition or alteration is effected to such electric fence system; or

- there is a change of ownership of the premises on which such electric fence system exists after 1 July 2020, the user shall obtain an electric fence system certificate for the electric fence system, and where after the provisions of subregulation (4) shall be applicable.

- Issuing of electric fence system certificate

(1)  Only a registered person may issue an electric fence system certificate in the form of Annexure 1, after having satisfied himself or herself by means of an inspection and test that;

(a)  the new electric fence system complies with the provisions of regulation 12(1);

- an electric fence system which existed prior to the incorporation of the relevant health and safety standard contemplated in regulation 12( 1) into these Regulations complies with the general safety principles of such standard; or

- an electric fence system which existed prior to the incorporation of the relevant   health and safety standard contemplated in regulation 12(1) into these Regulations and to which extensions or alterations have been effected, that-

(i)	the affected part of the system complies with the general safety principles of such standard, and

- the extensions or alterations effected comply with the provisions of regulation 12( 1):

Provided that a user of a pet-shock system or strip-grazing electric fence system, who is competent to install such a system, may issue an electric fence certificate for a pet-shock system or strip-grazing electric fence system, as the case may be.

(2) If at any time prior to the issuing of an electric fence system certificate in terms of regulation 13(1), any fault or defect is detected in any part of the system, the registered person shall refuse to issue such certificate: Provided that if such fault or defect in the opinion of the registered person constitutes an immediate danger to persons in the case where electricity is already supplied, he or she shall forthwith notify the user or lessor, as the case may be, in writing

- Any person who undertakes to install, alter or extend an electric fence system shall ensure that an electric fence system certificate is issued for that work.

- No person shall amend an electric fence system certificate issued by a registered person.

- Application for registration as registered person

(1)   Application for registration as a registered person shall be made to the chief inspector in the form of Annexure 2, and shall be accompanied by the registration fee prescribed by regulation 23.

- Any natural person who satisfies the chief inspector that he or she meet the registration criteria and has sufficient knowledge of the safety standards applicable to electric fence systems may be registered by the chief inspector as a registered person.

- The chief inspector shall furnish a registered person with a certificate of registration, and enter such registration into the national database.

- A registered person shall on request produce his or her certificate of registration to any inspector and any supplier or any person for whom he or she intends to install an electric fence system and issue an electric fence certificate.

- Withdrawal of registration and approval

(1) Subject to the provisions of subregulation (2), the chief inspector may withdraw a registration or an approval issued to an approved inspection authority or to a registered person if such a person -

- no longer complies with any of the conditions referred to in regulation 14(2) or 17(1), respectively; or

(b)  is convicted of an offence referred to in regulation 24.

- The chief inspector may not withdraw a registration or an approval unless he or she    has -

- informed the holder of such registration or approval of the intended withdrawal thereof and of the grounds upon which it is based; and

- afforded such holder a reasonable opportunity to state his or her case and, if the holder is a person referred to in subregulation (1)(a), afforded such holder an opportunity to comply with those conditions within the period specified by the chief inspector.

- The chief inspector shall, in writing, inform the person concerned of the reasons for his or her decision.

- Any person adversely affected by a decision of the chief inspector may, in writing, appeal to the Director-General against such decision.

- An appeal referred to in subregulation (4) shall-

- be lodged within 60 days from the date on which the decision was made known; and

- set out the grounds of appeal.

- After considering the grounds of appeal and the chief inspector's reasons for his or her decision, the Director-General shall as soon as practicable confirm, set aside or amend the decision.

16. Substitution of lost, damaged or destroyed certificate of registration

(1) A registered person whose registration certificate issued in terms of regulation 14 has been lost, damaged or destroyed, may apply for a duplicate in the form of Annexure 2.

- The application referred to in sub regulation (1) shall be accompanied by the fee prescribed by regulation 23.

- After submission of proof that a certificate of registration has been lost, damaged or destroyed, the chief inspector shall issue a substitute therefor on which the word "duplicate" shall appear.

- Inspection authorities

(1) On application, the chief inspector may approve as an inspection authority any person that has been accredited by the accreditation authority to be an approved inspection authority for performing the prescribed functions with regard to the manufacture or testing of electrical machinery.

(2) An application referred to in subregulation (1) shall be made to the chief inspector in the form of Annexure 3 and shall be accompanied by;

- a certified copy of the accreditation certificate issued by the accreditation authority; and

- the fee prescribed by regulation 23.

  - Earthing

(1)  An employer or user shall cause;

- roofs, gutters, downpipes and waste pipes on premises to which electrical energy is supplied to be earthed, except;

    - where the operating voltage does not exceed 50 V;

    - roofs made of non-conductive material or metal roofs covered by non-conductive material;

    - gutters, downpipes and waste pipes made of non-conductive material or gutters and downpipes attached to a metal roof which is covered by non-conductive material;

    - roofs, gutters, downpipes and waste pipes on premises which receive electricity by means of underground service connections: Provided that the connection is to the conductive structures;

- all accessible metallic parts of electrical machinery that, though normally not forming part of an electrical circuit, may become live accidentally, to be protected by an insulating covering or to be otherwise enclosed or to be earthed and the resistance of the earth continuity path shall not exceed 0,2 ohm, except-

    - metal in earth-free situations, other than runs of metal wireway, and the close-fitting metal sheathing and armouring of cables;

    - short separate lengths of heavy-gauge metal wire way used for the mechanical protection of cables where such cables are not used in the secondary circuits of discharge luminaire installations;

    - short, unexposed separate lengths of metal wire way used for the mechanical protection of insulated wiring passing through walls, floors, partitions or ceilings;

    - metalwork of fixed electrical machinery where such metalwork is more than 2.4 m above the floor: Provided that this exception shall not apply where such metalwork is situated in any position likely to become damp, or in an elevator shaft, or near rotating machinery, or in contact with a wall, ceiling or other support constructed of or covered with conducting material;

    - metal parts of electrical machinery where such parts are enclosed or shrouded by insulating material so that such metal parts cannot be touched;

  - cleats, clips, saddles, clamps of other devices for fixing wireways and cables;

  - shades, reflectors and guards supported on lamp holders or discharge luminaires;

  - lamp caps;

- metal parts of or screws in or through non-conducting materials which are separated by such materials from current-carrying parts and from earthed non-current-carrying parts in such a way that in normal use they cannot become live or come into contact with earthed parts.

- If at any time through a test of any electrical machinery on the premises by the supplier or inspector it is found that exposed metallic parts of the electrical installations are not earthed, the supplier or inspector shall require the occupier or owner of such premises to effect the necessary earthing within a fixed period of time not exceeding 30 days and, should the occupier or owner fail to effect the necessary earthing, the supplier may disconnect the electrical energy to such premises and shall not reconnect such energy until the earthing has been carried out.

  - Overhead power lines

(1) A supplier, employer or user shall cause the supports, clearances, insulators and fittings and conductors for power lines to be designed, installed and maintained in accordance with the relevant health and safety standard incorporated into these Regulations under section 44 of the Act.

- The supplier, employer or user shall cause the distance of any power line from an explosives magazine to comply with the requirements of the Explosives Act, 1956 (Act No. 26 of 1956).

- A supplier, employer or user shall cause the clearance of conductors and other wires over the normal high-water level of power lines crossing over water to be not less than the values for power lines above the ground outside townships: Provided that if the owner of the land on which the water is situated requires a greater clearance and no agreement between the supplier, user or owner of the land can be reached, the dispute shall be referred to the chief inspector for a decision.

(4) 	No person shall construct any road, railway, tramway, communication line, other power line, building or structure, or place any material or soil under or in the vicinity of a power line, which will encroach on the appropriate minimum clearances required in terms of subregulation (1).

(5)  No person shall encroach in person or with objects on the minimum safety clearances required in terms of subregulation (1) or require or permit any other person to do so except by permission of the supplier, employer or user operating the power line.

(6)  The supplier or user of power lines shall control vegetation in order to prevent it from   encroaching on the minimum safety clearance of the power lines and the owner of the vegetation shall permit such control.

(7)  The employer or user shall ensure that all supports of the lattice type which are used to carry overhead conductors or live parts of other electrical equipment are adequately protected in order to prevent any unauthorized person from coming into dangerous proximity of the conductors by climbing such supports, and an inspector may require an employer or user similarly to protect a support of any other type.

- Service connections

(1) No person shall require or permit any overhead service connection to be connected to the supplier's conductors elsewhere than at a point of support.

(2) No supplier, employer or user shall connect electrical energy to premises other than by means of conductors complying with the relevant health and safety standard incorporated into these Regulations under section 44 of the Act and by means of a safe connection to the premises.

- Overhead line crossings

(1) Where a power line crosses a proclaimed road, railway or tramway, or a conductive communication line, the supplier, employer or user shall cause the clearance to comply with the requirements of regulation 19, and shall further cause-

- every structure supporting a crossing span to be designed in such a manner that it will be able to withstand the loads that may be imposed upon it should a breakage of any phase conductor or earth conductor occur;

- every structure supporting a crossing span, as far as is reasonably practicable, to be located so that it will not touch the service crossed, should it overturn;

- subject to the restrictions referred to in paragraph (b), one of the structures supporting a crossing span to be located as close to the point of crossing as is reasonably practicable;

- the clearance of the crossing span where it crosses a proclaimed road to be not less than 4,5 m in the case of a broken-phase conductor in a span other than the crossing span;

- armour rods, arcing horns or other proven methods to be fitted at the live ends of suspension and rigid insulators on at least the first three structures on each side of the crossing if the maximum voltage for which the power line is designed exceeds 1,1 kV rms ; alternatively, duplicate conductors, tied together at intervals of not more than 1 ,5 m shall be provided in the crossing span and shall be supported by duplicate parallel insulators, and for lines on rigid insulators the duplicate conductors shall extend at least 1,5 m beyond the supports on each side of the crossing span; and

- all crossings over services, including conductive communication lines, shall be mutually agreed between the power line user or supplier and the communications line user or user of other services.

- The supplier, employer or user shall cause every overhead service connection that crosses over bare conductive communication lines of the communication network to have minimum clearances between the overhead service connection and the conductive communication lines at the points of crossing of 0,5 m and the overhead service connection shall not cross below bare conductive communication lines.

- Bare conductors on premises

The employer or user shall cause bare conductors, other than conductors of a power line which cannot be completely insulated and which is installed on premises, to be so placed as to prevent accidental contact therewith and warning notices to be prominently displayed at such conductors.

- Fees payable

The fees payable in respect of an application in terms of regulations 14(1) and 17(2) (b) or a duplicate certificate of registration in terms of regulation 16(2) shall be N$200.

- Offences and penalties

Any person who contravenes or fails to comply with any of the provisions of regulations 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14(4), 18, 19, 20,21 and 22 shall be guilty of an offence and liable upon conviction to a fine or to imprisonment for a maximum of 12 months and, in case of a continuous offence, to an additional fine of R200 for each day on which the offence continues or additional imprisonment of one day for each day on which the offence continues: Provided that the period of such additional imprisonment shall not exceed 90 days.

- Short title

These Regulations shall be called the Electrical Machinery Regulations, 2021, and shall commence on 1 July 2021: Provided that regulation 12(4) shall commence on 1 July 2021.

Annexure 1

LABOUR ACT, 2007

REGULATION RELATING TO THE HEALTH AND SAFETY OF EMPLOYEES AT WORK, 1997

CERTIFICATE OF COMPLIANCE FOR ELECTRIC FENCE

| Electric Fence System Certificate of Compliance in accordance with regulation 12(4) and 13(1) of the Electrical Machinery Regulations, 2019. | Certificate number: ……………………………….. |
| --- | --- |
| Type of certificate (tick in the box) | Initial certificate |  | Supplementary certificate |  |
| Supplement No. ...................... to Initial Certificate No. .................. as issued on: ……………………………..….. |
| Installation details |
| Name of building |  |
| Physical address |  |
| ERF or Lot number |  | Installation pole number |  |
| Town |  | GPS Coordinates |  |
| Declaration by registered electrical fence installer |
| Full name and surname |  |
| ID number |  |
| Registration number and date of registration |  |
| Address |  |
| Contact phone numbers |  |
| Email |  |
| I, …………………………………………………………………………………. ID No. ……………………………………………………………………… a registered electric fence system installer, declare that I have personally carried out the inspection and testing of the electric fence system described above as per the requirements of regulation 13(1), and deem the installation to be reasonably safe when properly used. Signature: ……………………………………………………. Date: ……………………………….. |
| Declaration by user |
| I, ………………………………………………………………………………….. ID No. ………..………………………………………………………….. declare that I am aware of my responsibilities in terms of regulation 12 of Electrical Machinery Regulation and undertake to operate and maintain the electric fence system in a safe manner. Signature: ……………………………………………………. Date: ……………………………………… |

Annexure 2

LABOUR ACT, 2007

REGULATION RELATING TO THE HEALTH AND SAFETY OF EMPLOYEES AT WORK, 1997

REGULATION 14(1) OF THE ELECTRICAL MACHINERY REGULATIONS

APPLICATION FOR REGISTRATION AS AN ELECTRIC FENCE SYSTEM

INSTALLER

|  |  | Ministry of Labour, Industrial Relations and Employment Creation Division of Occupational Health and Safety P Bag 19005 Khomasdal Windhoek |  |
| --- | --- | --- | --- |
| First names (block letters): ....................................................................... |
| Postal address: ......................................................................................... |
| Contact details: Cell No: ………………………… Tel No: ……………………………… |  |
| E-mail address: …………………………………………………. |  |
| Date of birth: ………………………………… |  |
| Place of birth: ………………………………. |  |

Identity number: ........................................

Note: A certified copy of electric fence system installer proficiency must be attached.

Two clear identical unmounted photographs of 40 mm by 30 mm showing the face and shoulders of the applicant to be submitted. One photograph to be certified on the back as follows:

I certify this to be a true photograph of. ................................................

Signature of Magistrate, Justice of the …………………………… Date ………………………...

Peace or Commissioner of Oaths ……………………………….

I hereby declare that the above particulars are, to the best of my knowledge and belief, correct.

Signature of applicant: ....................................	Date: ................................

SPECIMEN SIGNATURE OF APPLICANT

Note - The specimen signatures should be the normal signature of the applicant and should be carefully completed. One specimen will be affixed to any certificate of registration that may be issued.

| 1 | 2 | 3 |
| --- | --- | --- |

Annexure 3

LABOUR ACT, 2007

REGULATION RELATING TO THE HEALTH AND SAFETY OF EMPLOYEES AT WORK, 1997

REGISTRATION CRITERIA FOR ELECTRIC FENCE SYSTEM INSTALLER

REGISTRATION CRITERIA

INTRODUCTION

This document outlines the registration criteria that a person must comply with in order to be registered by the Chief Inspector as an Electric Fence System Installer as defined in the Electrical machinery Regulations, 2021, promulgated by Government Notice R xxx of 01 July 2021.

REQUIREMENTS FOR REGISTRATION

The applicant shall submit the following documents to the Chief Inspector to be considered for registration:

- Completed application form (annexure 2)

- Submit proof of having passed prescribed trade test for Electrician General in terms of both Namibia Training Authority and Namibia Qualifications Authority

- Submit documentary proof of successful completed skills programme on Electric Fence System Installers from an accredited training provider that consist out of the following unit standards as prescribed by Namibia Training Authority:

- Install electric fencing

- Demonstrate an understanding of electric fencing

- Apply cabling methods

- Use elementary electronics as applied to electronic systems

- Configure an installation

- Determine installation requirements

- Explain the use of installed systems.

- Copy of identification document

- Two photo’s colour or black & white

- Proof of payment

Note: All copies to be certified

Annexure 4

LABOUR ACT, 2007

REGULATION RELATING TO THE HEALTH AND SAFETY OF EMPLOYEES AT WORK, 1997

REGULATION 17(1) OF THE ELECTRICAL MACHINERY REGULATIONS

APPLICATION FOR APPROVAL AS AN APPROVED INSPECTION

AUTHORITY FOR ELECTRICAL MACHINERY

Ministry of Labour, Industrial Relations and Employment Creation

Division of Occupational Health and Safety

P Bag 19005

Khomasdal

Windhoek

- PARTICULARS OF APPLICANT

Surname: ...........................................................................................

First names: .......................................................................................

Id no.: ................................................................................................

Trading name: ...................................................................................

State whether the business is a sole proprietorship/partnership/company/ close corporation (delete whichever is not applicable).

Business Reg. no.: ................................................................................

Region in which business is situated: ....................................................

Physical address: .....................................................................

.....................................................................

Postal address: .........................................................................

........................................................................

Tel No.: .......................................... 	Cell. No.: .......................................................

Fax No.: ........................................... 	Email: ............................................................

- STATE TYPE OF REGISTRATION YOU HAVE:

SANAS REGISTRATION NUMBER: ..........................................................................

SCOPE OF ACCREDITATION: ..................................................................................

- IN SUPPORT OF THE APPLICATION, PLEASE SUBMIT THE FOLLOWING:

  - A certified copy of the business registration number (indicate Reg. No.);

  - A certified copy of the accreditation certificate from the accreditation authority.

I hereby declare that the above particulars are, to the best of my knowledge and belief, correct.

Signature of applicant: …………………………….     Date: ......................................

FOR OFFICE USE ONLY

Application: APPROVED/NOT APPROVED

Reason/s for declining: 	.............................................................................................

……………………………………………………………………

Registration No: ..............................................